## Slide 1: ​Flammable and Combustible Liquids Storage Safety GROUP HSE RULE (CR-GR-HSE-417)
EXECUTIVE SUMMARY
This rule defines the minimum HSE requirements to be implemented to manage risks associated with above-ground storage tanks containing flammable and combustible liquids.

## Slide 2
Purpose: This rule defines the minimum HSE requirements to follow for the management of risks related to facilities that store the following flammable and combustible liquids (“products”):
Crude oil, condensates, intermediate oil refining cuts;
Fuels (gasoline, kerosene, diesel, fuel oil, etc.);
Pure solvents, in mixture or with additives, and special petroleum fluids;
Ethanol or other biofuels components;
Other combustible products (bitumen, lubricants, etc.).
Scope of application: Applicable in all Group entities and affiliates. Does not concern the GRP branch.
This rule concerns installations with above-ground tanks located in sites:
With an overall capacity > 500 m3 of stored products; or
Containing at least one Class I product tank as defined in NFPA 30 (flash point less than 37.8 °C) with a unit capacity > 100 m3.
This rule does not apply to storage:
Of hydrocarbons in liquefied or refrigerated form (e.g. LPG, LNG) which are covered by another dedicated rule;
On floating supports (e.g. FPSO, FSO);
In vessels integrated within production units;
In mobile tanks (e.g. trucks, rail tank cars, large bulk containers);
In underground tanks;
In service stations tanks;
In above-ground tanks with a capacity < 5 m3.

## Slide 3
Replaces:
  REG-GR-SEC-029 Major REX Tank overfill prevention
  REG-GR-SEC-028 Major REX Lightning strike on storage tank
  CR-MS-HSEQ-332 Overfill prevention process
  CR-RC-HSE-016 Safety of flammable and combustible liquids storages
  GS-EP-SAF-341 Location and protection of onshore hydrocarbon storage
  CR-MS-HSE-352 Lightning risk
Date of publication in REFLEX: 30/09/2019
Date of application: 6 months after publication, except for:
Requirements that require work on tanks, to be carried out during the next internal inspection.
2 years for protection against pump overheating.

## Slide 4
REQUIREMENTS OVERVIEW: Authorised Tank Types
Construction Codes for Tanks (Requirement 3.1.1)
Tanks are constructed according to an industry code or standard recognised by the applicable local regulations.
Files of on-site tanks and associated retention are available.
EP-RC-MS : Work on documentation to be carried out for older sites, where some data could be missing.
Tank Classification According to Products (Requirement 3.1.2)
Tanks are identified and labelled according to the products they contain.
In the case of storage of different products in a common retention bund, their classification and the potential risks of a related leak of one or more of these products are taken into account.
No impact

## Slide 5
REQUIREMENTS OVERVIEW: Prevention of Loss of Containment
Protection Against Over-Pressure and Under-Pressure (Requirement 3.2.1)
Tanks are protected against pressure surges and under-pressure related to operating conditions.
Vertical tanks with a fixed roof are able to support a gradual increase in pressure due to fire in the retention without causing a rupture of the welding between the tank shell and tank floor.
No impact
Levels of Concern and Associated Alarms (Requirement 3.2.2)
For any Class I or Class II product tank with a capacity > 100 m3, the following levels of concern are established and documented:
  Critical High Level;
  Very High Level;
  High Level;
  Maximum Working Level.
Very High Level generates an alarm. For flammable liquids, the High Level also generates an alarm.
Any activation of High Level and Very High Level alarms during operations is logged.
The Maximum Working Level is always below the High Level. The use of High Level or Very High Level alarms for the management and monitoring of routine storage tanks filling operations is not authorised.
No impact

## Slide 6
REQUIREMENTS OVERVIEW: Prevention of Loss of Containment
Overflow Prevention (Requirement 3.2.3)
Any tank with flammable liquids that is filled by pipelines, ships/barges or rail tank cars is equipped with an:
Automatic Tank Gauge (ATG), which continuously measures the product level in the tank; and
Automatic Overflow Prevention System (AOPS):
  The AOPS conforms to the specifications in Appendix 1;
  When an AOPS is used, the site also has a means to physically stop the tank filling operation which is independent from the one used by the AOPS.
The equipment listed above is included in a preventative maintenance program, the frequency of which is justified. The monitoring of this maintenance is documented.
Any failure or inhibition of any of this equipment is systematically brought to the attention of the person in charge of the storage facilities.
EP-MS : no impact RC : moderate impact for sites with delivery by rail-way

## Slide 7
REQUIREMENTS OVERVIEW: Prevention of Loss of Containment
Secondary Containment (Requirement 3.2.4)
Secondary containment is provided for all tanks.
When the secondary containment is made up by a retention bund, it:
Is sufficiently water tight to hold the products for the time required for their recovery;
Has a capacity of no less than 100% of the maximum operating volume of the largest storage tank associated with the retention bund for all products, except for bitumen;
Has a surface area (net of reservoir footprint) that allows for efficient firefighting consistent with the expected scenarios.
No impact

## Slide 8
REQUIREMENTS OVERVIEW: Prevention of Loss of Containment
Leak Detection (Requirement 3.2.5)
For all sites with > 2500 T of storage capacity, secondary containment are equipped with a leak detection for gaseous and/or liquid products:
Systematically for flammable liquids;
According to risk analysis results for spills in retention of combustible liquids.
These detectors are included in a preventative maintenance program, the frequency of which is justified. The monitoring of this maintenance is documented.
No impact
Piping Protection (Requirement 3.2.6)
The piping connected to storage tanks are protected against the risks of overpressure due to the thermal expansion of the transported liquids.
If piping carrying products other than those associated with the tanks are routed within the retention bund, a risk analysis is conducted to define the risk control measures to put in place.
RC : no impact EP-MS : formalisation of an existing requirement within a GS and MS/AFR Invariant

## Slide 9
REQUIREMENTS OVERVIEW: Prevention of Loss of Containment
Pumping Station Protection (Requirement 3.2.7)
Pumping stations associated with storage are:
Fitted with retention and drainage adapted to the risks of spills;
Equipped with detection adapted to the risks of leaks;
Protected against overheating risks due to lack of flow, if they include automatic or remote operated pumps without supervision.
RC : already a regulatory requirement EP : requirement met in practice MS : new requirement

## Slide 10
REQUIREMENTS OVERVIEW: Prevention of Explosions and Fires
Area Classification (Requirement 3.3.1)
Storage facilities are subject to potentially explosive atmospheres area classification according to local regulations, or by default, according to the prescriptions of the European Directive « ATEX » n° 1999/92/CE or the international standard IEC60079-10-1.
No impact
Protection Against Risks Related to Lightning (Requirement 3.3.2)
All tanks and their accessory equipment are protected against lightning.
Fixed roof above-ground tanks without an internal floating screen, in which an explosive atmosphere is likely to form under normal operating conditions, have protection measures against explosion.
These measures are defined on the basis of a prior lightning risk analysis.
No impact

## Slide 11
REQUIREMENTS OVERVIEW: Prevention of Explosions and Fires
Protection Against Risks Related to Static Electricity (Requirement 3.3.3)
To avoid excessive accumulation of electrostatic charges in tanks containing products that may present a risk of explosion in the event of static electricity discharge, the linear speed of product transfer during tank filling adheres to the recommendations of API RP 2003.
No impact
Isolation Means in Case of Fire (Requirement 3.3.4)
Flammable liquids tanks are equipped with fireproof isolation means located as close as possible to the tank.
RC : no change
EP : application of GS-EP-SAF-341 within EP system
MS : already in place according to CR-MS-EXP-001

## Slide 12
REQUIREMENTS OVERVIEW: Prevention of Explosions and Fires
Firefighting (Requirement 3.3.5)
Storage of flammable and combustible liquids is equipped with firefighting means adapted to the quantities and nature of the products stored and the scenarios identified.
The firefighting means are sized, as a minimum, on the basis of the following scenarios:
Flammable and combustible liquids tank fires;
Flammable liquids retention fires;
Flammable and combustible liquids pumping station fires;
Cooling exposed tanks in case of fire, to prevent escalation.
No impact
Emergency Response Plan (Requirement 3.3.6)
All storage sites are covered by an emergency response plan that addresses fire and explosion scenarios as well as leaks and spills.
It contains emergency response cards which address, as a minimum, the following cases: overflow of a storage tank, product reaching a Very High Level in the tank, and detection of product in the secondary containment area.
It is regularly updated to reflect changes in layout, equipment and organisation and at least every 5 years.
No impact

## Slide 13
REQUIREMENTS OVERVIEW: Prevention of Explosions and Fires
Tests and Exercises (Requirement 3.3.7)
The firefighting means are operated during regular exercises, according to a frequency defined in the emergency response plan and at least once per year. These exercises are documented in written reports available on site.
No impact

## Slide 14
REQUIREMENTS OVERVIEW: Operations Safety
Operating Procedure (Requirement 3.4.1)
The operating procedure(s) includes as a minimum the following elements:
Planning aspects related to product movement;
Operating parameter monitoring and information to be exchanged between the participants during operations;
Supervision continuity,
Traceability of key information transmitted during handovers;
Communication means, including testing their reliability, to be able to stop product movements in case of emergency.
RC-MS : no impact EP : formalisation of certain operations to be planned (gauging, sampling,...)
Protection Against Low Levels (Requirement 3.4.2)
If a low level is likely to create a safety risk, any tank with a capacity > 100 m3, is equipped with a low level alarm device.
No impact

## Slide 15
REQUIREMENTS OVERVIEW: Operations Safety
Temperature Monitoring (Requirement 3.4.3)
Tanks in which the rise in temperature is likely to lead to dangerous phenomena are equipped with temperature sensors and associated alarms.
No impact
Control of Water Drainage (Requirement 3.4.4)
When water drainage from tanks is required, it is carried out in a controlled manner.
No impact
Control of Access to Tank Roofs (Requirement 3.4.5)
A document defines the conditions for allowing access to tank roofs. It mentions as a minimum the acceptable atmospheric or operating conditions, the PPE and the safety measures to be implemented.
RC-MS : no impact EP : formalisation de certaines opérations à prévoir

## Slide 16
REQUIREMENTS OVERVIEW: Operations Safety
Gauging (Requirement 3.4.6)
Measurement or sampling operations from the tank roof are subject to a procedure, which takes into account the risks associated with the characteristics of the products and tank configuration and which specifies:
Settling time period to be respected after product movements;
Equipment to use;
Operating conditions (limitations during storms, product movement in the tank, etc.).
RC-MS : no impact EP : formalisation to be planned