## Slide 1: HSE Requirements for the Isolation of Powered Systems GROUP RULE (CR-GR-HSE-428)
Summary
This rule defines the minimum HSE requirements to be respected when preparing, implementing and organization of the powered systems isolation process.

## Slide 2
Context :
    Between 2010 and 2019, 41 fatal accidents (excluding transport and Process safety - 37) recorded in the Group
    29% of these accidents are due to the failure of isolation of powered systems
    93% of the victims are contractors
Scope of application : All operated Group entities and affiliates;
Definition of 16 requirements, grouped into 5 themes :
    Organisation of the Isolation Process
    Preparation
    Implementation of Isolation
    De-isolation
    Audits and Performance Improvement
Replacing Group and Branch Documents:
    DIRSEC 07 - Isolation of Energy Sources and hazardous substances before Work
    CR-EP-EXP-418 - Process, mechanical and electrical isolations
    CR-RC-HSE-028 - Isolation rules for sources of hazardous substances
    Partially CR-MS-HSEQ-202 - High-risk operations and works (§6. Line or Equipment opening- §8. Working on hazardous machinery- §9 Work on electrical installations)
Publication in REFLEX : 18/01/2021
Effective date : 18/01/2022
CR-GR-HSE-428

## Slide 3
REQUIREMENTS REVIEW
{Requirement 3.1.1: Isolation Procedures
The isolation process for powered systems is described, for each type of isolation, in a documented procedure which includes the requirements of this rule as a minimum.
{Requirement 3.1.2: Roles and Assignments
The distribution of roles and assignments for people involved in implementing the isolation process, as well as the possibilities for delegation, is clearly defined and communicated to the relevant personnel in the entity or affiliate and to contractors, so that they can inform their personnel.
GRP : new requirement
MS, RC : roles were defined but not the possibilities of delegation
GRP: new requirement

## Slide 4
REQUIREMENTS REVIEW
{Requirement 3.1.3: Training and Certification
Everyone, including contractor personnel, with a role in the isolation process is trained and certified to execute their role. The certification is documented and issued after a competency assessment. A list of trained and certified personnel for each type of isolation is kept up to date. The frequency of refresher training, at least every 5 years, is determined by the isolation procedure.
GRP, RC: certification after a competency assessment and updating the list of trained and certified personnel are new requirements
Training of contractor personnel involved in the isolation process and the frequency of refresher training, at least every 5 years, are new requirements for all branches
NEW

## Slide 5
REQUIREMENTS REVIEW
{Requirement 3.2.1: Risk Analysis for Isolation
An isolation is based on a documented risk analysis. This risk analysis is validated by a visit to the worksite to physically identify the equipment and installations concerned by the isolation.
GRP : new requirement

## Slide 6
REQUIREMENTS REVIEW
{{Requirement 3.2.2: Selecting Isolation Devices
Isolation devices are selected according to criteria defined in the isolation procedure of the entity or affiliate, considering the risk analysis. The minimum criteria for process isolation devices are defined: In Appendix 3 for the EP branch By SIOPE matrix (Safe Isolation Of Plant and Equipment) in Appendix 4 for GRP, MS and RC branches. A positive isolation device, located as close as possible to the work site, is required as a minimum standard for: Hot works with naked flame on equipment and installations having contained flammable, toxic or hazardous products; Confined space entry); Long-term isolation.
GRP : new requirement
GRP, MS, RC : the use of the SIOPE matrix and the positive isolation device in the case of long-term isolation are new requirements. Note that some RC platforms already use the SIOPE matrix

## Slide 7
REQUIREMENTS REVIEW
{Requirement 3.2.3: Isolation Work Pack
In accordance with the risk analysis, isolation diagrams are drawn up. They are based on up-to-date plans and documents and verified at the worksite. An isolation work pack approved by the Approving Authority is compiled. This work pack is updated according to the evolution of isolation operations at the worksite and is accessible to all people concerned
GRP, MS : new requirement

## Slide 8
REQUIREMENTS REVIEW
{Requirement 3.3.1: Separation
The isolation devices defined in the isolation work pack are put in place to separate the equipment or the installation from its energy sources.
{Requirement 3.3.2: Lock-out - Tag-out
The isolation devices implemented in the separation phase are locked out and tagged out by the Isolating Authority. They are verified at the worksite by the Performing Authority. For electrical isolation, the isolation device is also locked out by the Performing Authority. If lock out by the Performing Authority is not possible, the Isolating Authority padlock key is secured in a lock-out box. Additional risk control measures are implemented if an isolation device cannot be locked out.
GRP, MS, RC : electrical lock-out by the performing authority or the securing of isolating authority padlock in a lock out box is a new requirement
Implementing additional risk control measures if an isolation device cannot be locked is a new requirement for all branches
GRP : new requirement
NEW

## Slide 9
REQUIREMENTS REVIEW
{Requirement 3.3.3: Releasing Stored Energy
Before any intervention, the energy stored in the isolated system is released.
{Requirement 3.3.4: Checking for the Absence of Energy
Before any intervention, the Isolating Authority and the Performing Authority check the absence of energy at the worksite. If it is impossible to check for the absence of energy, and if that has not been identified in a preparation step, the intervention is stopped, and a new risk analysis is performed.
GRP : new requirement
GRP : new requirement
EP, MS : stopping intervention and performing a new risk analysis if it is impossible to check for the absence of energy is a nex requirement

## Slide 10
REQUIREMENTS REVIEW
{Requirement 3.3.5: Worksite Monitoring of the Implementation of Process Isolation Devices
When a process isolation device is used, the Isolating Authority is present at the worksite to monitor the: Initial opening of the line; Installation of a special isolation device.
{Requirement 3.3.6: Isolation Device Shared by Several Isolations
If an isolation device is identified in several isolation certificates, the Approving Authority that authorised its installation, monitors it until its removal (at the end of all work). For each isolation certificate, the tag-out device is different.
EP,GRP, MS: new requirement
GRP, MS: new requirement

## Slide 11
REQUIREMENTS REVIEW
{Requirement 3.4.1: De-isolation
Any de-isolation, even temporary, is recorded on the isolation certificate In order to carry out tests, temporary de-isolations are possible without closing the associated permit to work. Such temporary tests are validated by the Approving Authority. All isolation devices, lock-out devices and tag-out devices are removed: When all the works covered by these isolation devices are finished and the corresponding permits to work have been closed out; By the Isolating Authority after the removal of any lock-out devices and tag-out devices by the Performing Authority.
GRP: new requirement
MS, RC : temporary de-isolation is a new requirement

## Slide 12
REQUIREMENTS REVIEW
NEW
{Requirement 3.5.1: Personal Isolation
A personal isolation is implemented for recurrent works with a low level of risk, for a maximum duration of one shift or day according to the entity or affiliate work regime. For any work not completed at the end of the shift or at the end of the day, the equipment or installation is returned to normal operational status (reconnection) or a full isolation is implemented. A personal isolation is not handed to another Isolating Authority. A personal Isolating Authority may only have a personal isolation in place on one piece of equipment at a time. An exhaustive list of equipment that can be covered by a personal isolation is established after a specific risk analysis and included in the entity's or affiliate's procedure.
{Requirement 3.6.1: Long-term Isolation
Long-term isolation devices are identified on diagrams and P&IDs, listed in a dedicated register and inspected at least once every quarter. Removal of long-term isolation devices requires a: A site joint site visit to be carried out by the Isolating Authority and the Performing Authority to ensure that isolation devices are suitable for the proposed work to be carried out; A permit to work.
New requirement for all the branches
GRP, MS, RC: new requirement

## Slide 13
REQUIREMENTS REVIEW
{Requirement 3.7.1: Internal Audits and Performance Improvement
An audit programme is put in place in the entity or affiliate, to make sure that the isolation procedure is applied. Isolation performance indicators, including as a minimum verification with the help of dedicated checklists, are defined and monitored. These indicators are analysed during a process review at least once a year. The review gives rise to an action plan to improve the process.
GRP, MS: new requirement